1. Predmet ponude

Predmet ponude je revitalizacija, odnosno zamjena svih modularnih komponenti APC ups uredjaja tipa Symmetra, koji se nalaze u Data centru MTKC i ANEX-u MTKC-prostor kolokacija,  prema definisanim tehničkim specifikacijama i lokacijama navedenim u prilogu 2.

2. Tehničke specifikacije

Usluga revitalizacije obuhvata:

- Dolazak APC Schneider sertifikovanog tima na lice mjesta za realizaciju usluge

- Zamjenu svih starih modularnih komponenti:

UPS Network Management Card with PowerChute Network Shutdown

APC PowerView UPS Management Display Rack Mount - Spare Part

Modular Power Revitalization Service Labor for (1) Symmetra PX 40k Frame

System Power Supply Unit For PX2 - Spare Part

Symmetra PX Battery Monitoring Card - Spare Part

Symmetra PX Display and Computer Interface - Spare Part

Symmetra PX SW Gear Monitoring Card - Spare Part

Symmetra PX XR Communication Card - Spare Part

Symmetra PX Intelligence Module - Spare Part

POWER MODULE FOR 10/16kW 400v SYMMETRA PX - SPARE PART

Symmetra PX 40kW Static Switch Module, 400V - Spare Part

Sve komponente i djelovi  moraju biti originalni, od APC Schneider proizvodjaca.

- Konfiguracija sistema i funkcionalna provjera

- Preuzimanje i transport iskoristenih komponenti do odobrenog centra za reciklazu i odlaganje

- Potrebno je obezbijediti godinu dana servis i podrsku za svaki od predmetnih upseva koji ukljucuje on site pregled, djelove, preventivni pregled itd..

3. Implementacija, acceptance test

Instalacija, povezivanje opreme i puštanje u rad vrši osoblje koje posjeduje odgovarajući sertifikat od strane proizvođača opreme-APC Schneider. Ponuđač mora dostaviti dokaze u pismenoj formi o kvalifikovanosti i ovlašćenju servisera od strane proizvođača opreme.

Zamjenu svih komponenti treba odraditi bez prekida rada ups uredjaja i u nocnom terminu od 00:00h-06:00h.

Nakon zamjene, odraditi konfiguraciju sistema i funkcionalnu provjeru.

Sve stare komponente preuzima ponudjac i transportuje dalje u odobreni centar za reciklazu i odlaganje.

Nakon zavrsenih radova izdati acceptance test za svaki od uredjaja.

4. Garancija i podrška u garantnom roku

Minimalna potrebna garancija od 1 godine na sve zamijenjene komponente.

Ponuđač mora priložiti garanciju u pismenoj formi da je spreman da u garantnom roku ponudi 24/7 podršku baziranu na rješavanju problema sledeći radni dan, sa obezbijeđenim servisom na teritoriji CG.

5. Tehnička dokumentacija

Ponuđač mora obezbijediti cjelokupnu tehničku dokumentaciju u lako čitljivom formatu u elektronskoj formi.